{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["Pump Selection Guide"],"not_rendered":{"images":1,"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Pump Selection Guide","index":0,"n_rows":125,"n_cols":33,"rows_kept":125,"merged":[[1,1,1,9],[2,17,2,32],[4,17,4,32],[6,6,6,9],[8,6,8,8],[10,6,10,8],[14,20,14,21],[14,22,14,24],[14,25,14,27],[14,28,14,30]],"flags":["formulas_cached_only"]}
[]
[null,"Pump Selection Guide"]
[{"$nulls":14},"Lists:",null,null,"size"]
[{"$nulls":16},"Select Mainline Size","0.5\"","0.75\"","1\"","1.25\"","1.5\"","2\"","2.5\"","3\"","4\"","5\"","6\"","8\"","10\"","12\"","14\"","16\""]
[null,null,20,null,"Elevation, ft (from water source to highest, farthest sprinkler)",{"$nulls":9},"Select Type of Pipe","C value",null,"ID"]
[null,null,"1\"",null,"Main Line Size, in",{"$nulls":9},"Class 160",150,0,"","","","","","","","","","","","","","","",""]
[null,null,"Class 200",null,"Type of Pipe Used",null,"",{"$nulls":7},"Class 200",150,1.189,"","",1.189,"","","","","","","","","","","","",""]
[null,null,350,null,"Main Line Length, ft",{"$nulls":9},"Sch 40",150,1.049,"","",1.049,"","","","","","","","","","","","",""]
[null,null,"1\" Rainbird DV",null,"Type of Valve",null,"",{"$nulls":7},"Sch 80 ",150,0.957,"","",0.957,"","","","","","","","","","","","",""]
[null,null,45,null,"Desired Pressure, PSI",{"$nulls":4},"Velocity in Pipe",{"$nulls":4},"Type K Copper",140,0.995,"","",0.995,"","","","","","","","","","","","",""]
[null,null,15,null,"Desired Flow, GPM",null,"",null,null,"4.329 ft/sec"]
[null,null,{"v":155.06486842289294,"d":"155.1"},null,"Total Dynamic Head (TDH), ft",{"$nulls":4},"PSI Loss in Run of Pipe",{"$nulls":6},"ID of selection",null,"psi loss in run of pipe",null,"velocity in pipe"]
[null,null,"0.9 hp",null,"Horsepower Required",{"$nulls":4},"9.67 psi",{"$nulls":6},1.189,null,9.669640009910367,null,4.329001266869487]
[]
[{"$nulls":19},"GPM","DV valve",null,"PGA valve (globe)",null,null,"PGA valve (angle)",null,null,"PEB valve"]
[null,"Click for Curve","SRHMSF",null,"Pumps Available:",{"$nulls":9},"Select Valve Type","max flow","min flow","psi loss","size",null,"3/4\"","1\"","1\"","1.5\"","2\"","1\"","1.5\"","2\"","1\"","1.5\"","2\""]
[null,"Click for Curve","BESSHM2",null,"(pump(s) listed may not be ideal, ask a W.P. Law professional for best selection)",{"$nulls":9}," 3/4\" Rainbird DV",22,0.2,5,null,1,3.2,3.3,5.1,null,null,4.3,null,null,1.3,null,null,1]
[null,"Click for Curve","MULP1502B",{"$nulls":11},"1\" Rainbird DV",40,0.2,3.8,null,3,3.9,3.6,5.3,{"$nulls":8},3]
[null,null,0,{"$nulls":11},"1\" Rainbird PEB",50,5,1.8,null,5,4.2,3.8,5.5,null,null,5,null,null,1.7,null,null,5]
[{"$nulls":14},"1\" Rainbird PGA \"angle\"",40,5,5.5,null,10,5,3.8,5.9,null,null,5.5,null,null,1.8,null,null,10]
[{"$nulls":14},"1\" Rainbird PGA \"globe\"",40,5,5.9,null,20,7.7,5.1,6,null,null,5.6,null,null,2.9,3.9,null,20]
[{"$nulls":14},"1.5\" Rainbird PEB",150,10,"",null,30,null,6.4,6.4,1.9,null,5.5,1.3,null,5.6,3.6,null,30]
[{"$nulls":14},"1.5\" Rainbird PGA \"angle\"",100,30,"",null,40,null,8.6,7,3.2,1.2,7.5,2,1,10,3.5,null,40]
[{"$nulls":14},"1.5\" Rainbird PGA \"globe\"",100,30,"",null,50,{"$nulls":3},4.8,1.5,null,3,0.9,15.6,3.6,4.8,50]
[{"$nulls":14},"2\" Rainbird PEB",200,75,"",null,75,{"$nulls":3},11.1,3,null,6.5,1.7,null,5.4,4.5,75]
[{"$nulls":14},"2\" Rainbird PGA \"angle\"",150,40,"",null,100,{"$nulls":3},19.2,5.5,null,11.7,3,null,9.6,5.2,100]
[{"$nulls":14},"2\" Rainbird PGA \"globe\"",150,40,"",null,125,{"$nulls":4},8.6,null,null,4.8,null,14.6,8.2,125]
[{"$nulls":19},150,{"$nulls":4},12,null,null,6.5,null,21.2,11.8,150]
[{"$nulls":14},"hp required",{"$nulls":4},175,{"$nulls":10},15.5,175]
[{"$nulls":14},0.903641424375833,{"$nulls":4},200,{"$nulls":10},19.5,200]
[{"$nulls":14},1]
[]
[{"$nulls":18},1,1.5,2]
[{"$nulls":18},"GDGT10","GDGT15","GDGT20",null,null,"file:///\\\\wplaw.wplawinc.com\\share\\departments\\website\\flash drive info\\reference charts\\pump info\\gould's gt curve.pdf","GDGT10",""]
[{"$nulls":19},"SRHMSF","MULP1502B",null,null,"file:///\\\\wplaw.wplawinc.com\\share\\departments\\website\\flash drive info\\reference charts\\pump info\\gould's gt curve.pdf","GDGT15",""]
[{"$nulls":20},"BESHM2",null,null,"file:///\\\\wplaw.wplawinc.com\\share\\departments\\website\\flash drive info\\reference charts\\pump info\\gould's gt curve.pdf","GDGT20",""]
[{"$nulls":23},"file:///\\\\wplaw.wplawinc.com\\share\\departments\\website\\flash drive info\\reference charts\\pump info\\MONROE PUMP CURVE.pdf","MULP1502B",45]
[{"$nulls":23},"file:///\\\\wplaw.wplawinc.com\\share\\departments\\website\\flash drive info\\reference charts\\pump info\\BESSHM2 CURVE.pdf","BESSHM2",40]
[{"$nulls":19},"TDH","GPM",null,null,"file:///\\\\wplaw.wplawinc.com\\share\\departments\\website\\flash drive info\\reference charts\\pump info\\SRHMSF CURVE.pdf","SRHMSF",15]
[{"$nulls":18},"GDGT10",45,55,10,0]
[{"$nulls":19},55,50,{"$nulls":3},"GDGT10",""]
[{"$nulls":19},70,45,{"$nulls":3},"GDGT15",""]
[{"$nulls":19},81,40,{"$nulls":3},"GDGT20",""]
[{"$nulls":19},90,35,{"$nulls":3},"MULP1502B",3]
[{"$nulls":19},97,30,{"$nulls":3},"BESSHM2",2]
[{"$nulls":19},103,25,{"$nulls":3},"SRHMSF",1]
[{"$nulls":19},107,20]
[{"$nulls":19},111,15]
[{"$nulls":19},115,10]
[{"$nulls":19},116,5]
[{"$nulls":19},117,0]
[{"$nulls":18},"GDGT15",75,60,0,0]
[{"$nulls":19},85,55]
[{"$nulls":19},93,50]
[{"$nulls":19},100,45]
[{"$nulls":19},104,40]
[{"$nulls":19},107,35]
[{"$nulls":19},110,30]
[{"$nulls":19},113,25]
[{"$nulls":19},115,20]
[{"$nulls":19},117,15]
[{"$nulls":19},119,10]
[{"$nulls":19},120,5]
[{"$nulls":19},121,0]
[{"$nulls":18},"GDGT20",65,85,0,0]
[{"$nulls":19},74,80]
[{"$nulls":19},82,75]
[{"$nulls":19},90,70]
[{"$nulls":19},98,65]
[{"$nulls":19},105,60]
[{"$nulls":19},110,55]
[{"$nulls":19},115,50]
[{"$nulls":19},119,45]
[{"$nulls":19},121,40]
[{"$nulls":19},123,35]
[{"$nulls":19},124,30]
[{"$nulls":19},125,15]
[{"$nulls":19},125,20]
[{"$nulls":19},125,25]
[{"$nulls":19},125.5,10]
[{"$nulls":19},125.7,5]
[{"$nulls":19},126,0]
[{"$nulls":18},"MULP1502B",97,80,45,1]
[{"$nulls":19},107,75]
[{"$nulls":19},115,70]
[{"$nulls":19},125,65]
[{"$nulls":19},135,60]
[{"$nulls":19},143,55]
[{"$nulls":19},150,50]
[{"$nulls":19},155,45]
[{"$nulls":19},160,40]
[{"$nulls":19},161,35]
[{"$nulls":19},163,30]
[{"$nulls":19},168,25]
[{"$nulls":19},170,20]
[{"$nulls":19},172,15]
[{"$nulls":19},175,10]
[{"$nulls":19},180,5]
[{"$nulls":19},185,0]
[{"$nulls":18},"BESSHM2",50,60,40,1]
[{"$nulls":19},75,55]
[{"$nulls":19},100,50]
[{"$nulls":19},125,45]
[{"$nulls":19},155,40]
[{"$nulls":19},175,35]
[{"$nulls":19},200,30]
[{"$nulls":19},210,25]
[{"$nulls":19},220,20]
[{"$nulls":19},230,15]
[{"$nulls":19},240,10]
[{"$nulls":19},245,5]
[{"$nulls":19},250,0]
[{"$nulls":18},"SRHMSF",50,60,15,1]
[{"$nulls":19},70,55]
[{"$nulls":19},85,50]
[{"$nulls":19},100,45]
[{"$nulls":19},110,40]
[{"$nulls":19},122,35]
[{"$nulls":19},133,30]
[{"$nulls":19},142,25]
[{"$nulls":19},150,20]
[{"$nulls":19},155,15]
[{"$nulls":19},160,10]
[{"$nulls":19},165,5]
[{"$nulls":19},167,0]